# Diesel Generator – Simulink Parameters and Calculated Values

This document summarizes the Simulink parameters of a Diesel Generator system including Synchronous Machine, Excitation System, Diesel Engine Governor, and Three-Phase Transformer. Relevant calculated base values are also provided.

## 1. Synchronous Generator Parameters

| Parameter | Value |
| --- | --- |
| Rated Power (Pn) | 1250 kVA |
| Rated Voltage (VLL) | 415 V |
| Frequency | 50 Hz |
| Stator Resistance Rs | 0.005 pu |
| Xd / Xq | 1.15 / 0.75 pu |
| Xd' / Xq' | 0.25 / 0.16 pu |
| Xd'' / Xq'' | 0.18 / 0.12 pu |
| Inertia Constant H | 2.5 s |
| Pole Pairs | 2 |

## 2. Excitation System (IEEE Type-1 AVR)

| Parameter | Value |
| --- | --- |
| Filter Time Constant Tr | 0.02 s |
| AVR Gain Ka | 300 |
| AVR Time Constant Ta | 0.001 s |
| Exciter Gain Ke | 1.0 |
| Exciter Time Constant Te | 0 s |
| Output Limits | ±11.5 pu |

## 3. Diesel Engine Governor Parameters

| Parameter | Value |
| --- | --- |
| Governor Gain K | 29 |
| Time Constants T1 T2 T3 | 0.01, 0.02, 0.2 s |
| Actuator Time Constants | 0.25, 0.009, 0.0384 s |
| Torque Limits | 0 to 1.1 pu |
| Engine Delay Td | 0.024 s |

## 4. Transformer Parameters

| Parameter | Value |
| --- | --- |
| Rated Power | 1250 kVA |
| Primary Voltage | 415 V |
| Secondary Voltage | 415 V |
| Primary Resistance | 0.003 pu |
| Secondary Resistance | 0.0001 pu |
| Magnetizing Resistance | 350 pu |
| Magnetizing Inductance | 0.4 pu |

## 5. Base Value Calculations

Base Power (Sbase) = 1250 kVA
Base Line Voltage (Vbase) = 415 V
Base Current (Ibase) = Sbase / (√3 × Vbase)
Ibase ≈ 1250×10³ / (√3 × 415) ≈ 1738 A

These base values are used for per-unit conversion of machine, excitation, governor, and transformer parameters.