Simulink parameters:

Solar side:

| Category | Parameter | Value |
| --- | --- | --- |
| Array | Parallel strings | 44 |
| Array | Series modules/string | 18 |
| Module | Pmax (W) | 214.65 |
| Module | Voc (V) | 36.3 |
| Module | Isc (A) | 7.84 |
| Module | Vmp (V) | 29 |
| Module | Imp (A) | 7.4017 |
| Module | Cells/module | 60 |
| Temp Coeff | dVoc/dT (%/°C) | –0.36099 |
| Temp Coeff | dIsc/dT (%/°C) | 0.102 |
| Model | IL (A) | 7.9095 |
| Model | I0 (A) | 2.9374e-10 |
| Model | Ideality factor | 0.98114 |
| Model | Rsh (Ω) | 294.02 |
| Model | Rs (Ω) | 0.3914 |

Wind side:

| Parameter | Value |
| --- | --- |
| Stator Resistance (Ohm) | 0.0485 |
| Armature Inductance (H) | 0.000395 |
| Flux Linkage (V.s) | 1.2 |
| Pole Pairs | 4 |
| Inertia (kg.m²) | 0.0027 |
| Nominal Power (W) | 300,000 |
| Base Wind Speed (m/s) | 12 |
| Max Power (pu) | 0.73 |

Synchronous Machine:

| Parameter | Value |
| --- | --- |
| Nominal Power Pn (VA) | 1250e3 |
| Line-to-line Voltage Vn (Vrms) | 415 |
| Frequency fn (Hz) | 50 |
| Reactances (pu) | Xd: 1.15, Xd': 0.25, Xd'': 0.18, Xq: 0.75, Xq': 0.16, Xl: 0.12 |
| d-axis Time Constant | Open-circuit |
| q-axis Time Constant | Short-circuit |
| Time constants [Tdo', Tdo'', Tq'] (s) | 3.5, 0.05, 0.04 |
| Stator resistance Rs (pu) | 0.005 |
| Inertia coefficient H (s) | 2.5 |
| Friction factor F (pu) | 0.01 |
| Pole pairs p | 2 |
| Initial conditions | ia, ib, ic (pu): 0, 0, 0; pha, phb, phc (deg): 0, 0, 0; Vf(pu): 1.0 |

Diesel Engine Governor:

| Parameter | Description / Definition | Value |
| --- | --- | --- |
| K | Regulator gain | 29 |
| T1 | Regulator time constant | 0.01 |
| T2 | Regulator time constant | 0.02 |
| T3 | Regulator time constant | 0.2 |
| T4 | Actuator time constant | 0.25 |
| T5 | Actuator time constant | 0.009 |
| T6 | Actuator time constant | 0.0384 |
| Tmin | Minimum torque limit | 0 |
| Tmax | Maximum torque limit | 1.1 |
| Td | Engine time delay | 0.024 |
| Pm0 | Initial mechanical power | 0.007343 |

Excitation System Parameters

| Parameter | Description | Value |
| --- | --- | --- |
| Tr | Low-pass filter time constant | 20e-3 (0.02) |
| Ka | Regulator gain | 300 |
| Ta | Regulator time constant | 0.001 |
| Ke | Exciter gain | 1 |
| Te | Exciter time constant | 0 |
| Tb | Transient gain reduction time constant | 0 |
| Tc | Transient gain reduction time constant | 0 |
| Kf | Damping filter gain | 0.001 |
| Tf | Damping filter time constant | 0.1 |
| Efmin | Minimum regulator output limit | -11.5 |
| Efmax | Maximum regulator output limit | 11.5 |
| Kp | Regulator proportional gain | 0 |
| Vt0 | Initial terminal voltage | 1 |
| Vf0 | Initial field voltage | 1.0072 |

Transformer side:

| Transformer Parameter | Value |
| --- | --- |
| Units | pu |
| Nominal power (Pn) | 1,250,000 |
| Nominal frequency (fn) | 50 |
| Winding 1 Parameter | Value |
| Phase-to-phase voltage (V1) | 415 |
| Resistance (R1) | 0.003 |
| Leakage inductance (L1) | 0.05 |
| Winding 2 Parameter | Value |
| Phase-to-phase voltage (V2) | 415 |
| Resistance (R2) | 0.0001 |
| Leakage inductance (L2) | 0.08 |
| Magnetization Branch Parameter | Value |
| Magnetization resistance (Rm) | 350 |
| Magnetization inductance (Lm) | 0.4 |

Boost converter side:

| Filter at solar side L C | 0.0093e-3 880e-6 |
| --- | --- |
| Filter at wind side R L C | 1.524 0.1e-3 880e-6 |
| Switching frequency | 15e3HZ |

EVFC side:

| Parameter | Value |
| --- | --- |
| Nominal Voltage (V) | 480 |
| Rated Capacity (Ah) | 100 |
| Initial State-of-Charge (%) | 60 |
| Battery Response Time (s) | 0.001 |
| Switching frequency | 20e3 |
| Filter Capacitance | 1000e-6 |
| BDC Resistance inductance | 5.1 100e-3 |
| Kpv, kiv | -5, -0.0005 |
| Kpi, kii | 5, 0.0005 |

Grid side

| Voltage | 400 |
| --- | --- |
| Frequency | 50 |
| Filter resistance inductance | 2.088 0.01e-3 |

Dstatcom side:

| Filter resistance inductance Capacitance | 0.1 1e-3 220e-6 |
| --- | --- |
| Dc voltage regulation Kp | 5 |
| Current regulation kpc kic | 800 1200 |
| Switching frequency | 20e3 |

Inverter side

| Filter inductance | 20e-3 |
| --- | --- |
| DC voltage regulation Kpd kid | 1 500 |
| Current regulation (Id, iq side) kpi kii | 0.5 200 |
| Switching frequency | 20e3 |